## 1. Load Schedule
BUILDING ELECTRICAL DISTRIBUTION SYSTEM
Load Schedule · 3-Storey Commercial Office Building · Ottawa, ON · Prepared by: A.Y. Loukili, Carleton University EE
Circuit ID | Load Description | Location | Qty | Unit Load (W) | Total Load (W) | Demand Factor | Design Load (W)
── LIGHTING ──
L1A | General Lighting | Floor 1 | 24 | 60 | 1440 | 0.85 | 1224
L1B | General Lighting | Floor 2 | 24 | 60 | 1440 | 0.85 | 1224
L1C | General Lighting | Floor 3 | 24 | 60 | 1440 | 0.85 | 1224
L2A | Task / Accent Lighting | Floor 1 | 10 | 40 | 400 | 0.8 | 320
L2B | Task / Accent Lighting | Floor 2 | 10 | 40 | 400 | 0.8 | 320
L2C | Task / Accent Lighting | Floor 3 | 10 | 40 | 400 | 0.8 | 320
── POWER RECEPTACLES ──
P1A | General Receptacles | Floor 1 | 36 | 180 | 6480 | 0.5 | 3240
P1B | General Receptacles | Floor 2 | 36 | 180 | 6480 | 0.5 | 3240
P1C | General Receptacles | Floor 3 | 36 | 180 | 6480 | 0.5 | 3240
P2A | Dedicated PC Circuits | Floor 1 | 12 | 300 | 3600 | 0.7 | 2520
P2B | Dedicated PC Circuits | Floor 2 | 12 | 300 | 3600 | 0.7 | 2520
P2C | Dedicated PC Circuits | Floor 3 | 12 | 300 | 3600 | 0.7 | 2520
── MECHANICAL ──
HVAC1 | Rooftop AHU — Unit 1 | Rooftop | 1 | 8000 | 8000 | 1 | 8000
HVAC2 | Rooftop AHU — Unit 2 | Rooftop | 1 | 6000 | 6000 | 1 | 6000
EV | Elevator Motor | Basement | 1 | 7500 | 7500 | 1 | 7500
── SAFETY SYSTEMS ──
EL | Emergency Lighting | All Floors | 14 | 40 | 560 | 1 | 560
FA | Fire Alarm Panel | Ground FL | 1 | 500 | 500 | 1 | 500
SEC | Security / Access Ctrl | All Floors | 1 | 800 | 800 | 1 | 800
TOTAL CONNECTED DESIGN LOAD | [6 empty] | 45272
Notes: Demand factors per Ontario Electrical Code (OEC) Table 8. Unit loads per NEC Table 220.12. All values in Watts (W) at 120/208V, 3-phase, 4-wire distribution.

## 2. Voltage Drop
VOLTAGE DROP ANALYSIS · Branch Circuits
Formula: VD (%) = (2 × L × I × R) / (1000 × V) × 100 ¦ OEC limit: ≤ 3% branch circuits, ≤ 5% total ¦ Conductor: Copper, 75°C
Circuit ID | Design Load (W) | Voltage (V) | Current (A) | Cable Size (AWG) | R (Ω/km) | Length (m) | VD (V) | VD (%) | Status
L1A | 1020 | 120 | 8.5 | #14 AWG | 10.45 | 35 | 6.2177 | 5.1815 | ✗ FAIL
L1B | 1020 | 120 | 8.5 | #14 AWG | 10.45 | 40 | 7.106 | 5.9217 | ✗ FAIL
L1C | 1020 | 120 | 8.5 | #14 AWG | 10.45 | 45 | 7.9943 | 6.6619 | ✗ FAIL
P1A | 2700 | 120 | 22.5 | #12 AWG | 6.56 | 30 | 8.856 | 7.38 | ✗ FAIL
P1B | 2700 | 120 | 22.5 | #12 AWG | 6.56 | 35 | 10.332 | 8.61 | ✗ FAIL
P1C | 2700 | 120 | 22.5 | #12 AWG | 6.56 | 40 | 11.808 | 9.84 | ✗ FAIL
P2A | 2520 | 120 | 21 | #12 AWG | 6.56 | 30 | 8.2656 | 6.888 | ✗ FAIL
HVAC1 | 8000 | 208 | 38.4615 | #6 AWG | 1.65 | 15 | 1.9038 | 0.91531 | ✓ PASS
HVAC2 | 6000 | 208 | 28.8462 | #6 AWG | 1.65 | 15 | 1.4279 | 0.68648 | ✓ PASS
EV | 7500 | 208 | 36.0577 | #6 AWG | 1.65 | 20 | 2.3798 | 1.1441 | ✓ PASS

## 3. Cable Sizing & Short-Circuit
CABLE SIZING & SHORT-CIRCUIT ANALYSIS
Short-circuit current: Isc = V / (√3 × Zs) ¦ Cable ampacity per NEC Table 310.15(B)(16), Cu 75°C, conduit
Circuit ID | Design Load (W) | Current (A) | Cable AWG | Ampacity (A) | Margin (%) | Conduit | Fault Level (kA) | Breaker Rating (A)
L1A | 1020 | 8.5 | #14 AWG | 15 | 43.3333 | 3/4" EMT | 10 | 15
L1B | 1020 | 8.5 | #14 AWG | 15 | 43.3333 | 3/4" EMT | 10 | 15
L1C | 1020 | 8.5 | #14 AWG | 15 | 43.3333 | 3/4" EMT | 10 | 15
P1A | 2700 | 22.5 | #12 AWG | 20 | -12.5 | 3/4" EMT | 10 | 20
P1B | 2700 | 22.5 | #12 AWG | 20 | -12.5 | 3/4" EMT | 10 | 20
P1C | 2700 | 22.5 | #12 AWG | 20 | -12.5 | 3/4" EMT | 10 | 20
P2A | 2520 | 21 | #12 AWG | 20 | -5 | 3/4" EMT | 10 | 20
HVAC1 | 8000 | 38.4615 | #6 AWG | 65 | 40.8284 | 1" EMT | 25 | 70
HVAC2 | 6000 | 28.8462 | #6 AWG | 65 | 55.6213 | 1" EMT | 25 | 70
EV | 7500 | 36.0577 | #6 AWG | 65 | 44.5266 | 1" EMT | 25 | 70

## 4. Cable Run Sheet
CABLE RUN SHEET · Building Electrical Distribution System
Cable Tag | From (Panel/DB) | To (Load) | Floor | Cable Type | Size | No. Conductors | Length (m) | Conduit | Conduit Size | Remarks
CB-L1A | MDB | LP-1A | B→1 | RW90 | #14 AWG | 3C | 35 | EMT | 3/4" | Lighting panel FL1
CB-L1B | MDB | LP-1B | B→2 | RW90 | #14 AWG | 3C | 40 | EMT | 3/4" | Lighting panel FL2
CB-L1C | MDB | LP-1C | B→3 | RW90 | #14 AWG | 3C | 45 | EMT | 3/4" | Lighting panel FL3
CB-P1A | MDB | PP-1A | B→1 | RW90 | #12 AWG | 3C | 30 | EMT | 3/4" | Power panel FL1
CB-P1B | MDB | PP-1B | B→2 | RW90 | #12 AWG | 3C | 35 | EMT | 3/4" | Power panel FL2
CB-P1C | MDB | PP-1C | B→3 | RW90 | #12 AWG | 3C | 40 | EMT | 3/4" | Power panel FL3
CB-H1 | MDB | HVAC-1 | B→R | RW90 | #6 AWG | 4C | 15 | EMT | 1" | AHU Unit 1, rooftop
CB-H2 | MDB | HVAC-2 | B→R | RW90 | #6 AWG | 4C | 15 | EMT | 1" | AHU Unit 2, rooftop
CB-EV | MDB | ELEV | B→R | RW90 | #6 AWG | 4C | 20 | EMT | 1" | Elevator motor
CB-EL | MDB | EL-PNL | B→M | RW90 | #14 AWG | 3C | 25 | EMT | 3/4" | Emergency lighting panel
CB-FA | MDB | FA-PNL | B→G | RW90 | #14 AWG | 3C | 10 | EMT | 3/4" | Fire alarm main panel
CB-UTL | UTIL | MDB | EXT | XLPE | 250 MCM | 4C | 12 | PVC | 3" | Utility service entrance
TOTAL CABLE LENGTH | [6 empty] | 322